## Sheet1
Transformer parameters
Top-oil rise over ambient temperature at rated load | 55 ℃
Winding hot-spot rise over top-oil temperature at rated load | 25 ℃
Oil time constant | 155 min
Winding time constant | 5 min
Ratio of load loss at rated load to no-load loss | 8
Maximum temperature limit of hot-spot temperature | 120 ℃
Cable parameters (nameplate capacity = 0.5514MVA)
Nominal cross-section of conductor | 630 mm2
Diameter of conductor | 28.3 mm
DC resistance of conductor at 20 ℃ | 0.0428 mΩ/m
Temperature coefficient of conductor | 0.00403 K-1
Burial depth | 800 mm
Thickness of insulation | 2.4 mm
Thickness of armour | 0.2 mm
Thickness of oversheath | 2.1725 mm
Thermal resistivity of insulation | 3.5 K∙m/W
Thermal resistivity of oversheath | 6 K∙m/W
Supply frequency | 50 Hz
Voltage to earth | 242 V
Special heat of conductor | 2.5*106 J/m3∙K
Special heat of insulation | 2.4*106 J/m3∙K
Special heat of armour | 3.45*106 J/m3∙K
Special heat of oversheath | 1.7*106 J/m3∙K
Maximum temperature limit of conductor | 90 ℃